Clarifications for NCCRD HPC datacenter

Tender No. : ICER/SH/2015-16/1003

Tender date: 8thFebruary, 2016

Note: All vendorsmust  include a signed copy with the company rubber stamp of this clarification document with the technical bid.

- Server room layout (ref. Technical specifications, section 1.0 and 1.1)

  - The height of the partition should match the height of the tallest piece of equipment, i.e. Battery rack or UPS to be located in the “UPS+Batteries area” such that air circulation between this area and the rest of the datacenter room is possible without additional cooling.

  - If this partition needs to extend all the way to the ceiling of the room, separate cooling for the UPS+Batteries area that is sufficient to manage the heat load in this part of the datacenter should be provided. A fireproof door separating the the “UPS+batteries” area and the server rack area should be provided.

  - Routing of power and cooling to server Racks.

    - Additional trenches for this purpose can be used in the design.

    - These additional trenches should not result in lowering of the overall floor level of the room

    - Spatial separation of between the trenches carrying power and network cables must be maintained as per existing standards for the same.

- UPS System (Technical specifications section 5.0 and 5.1)

  - No redundancy is needed for the UPS.

  - The power rating of the UPS can be between 40-45 kVA.

- Server/network racks (Technical specifications section  2.0 and 2.1)

  - The server rack width must be between 750-800 mm.

- PDU (Power distribution unit) (Technical specifications section 3.0 and 3.1)

  - The power supply cable should be atleast 3m in length and must be terminated with an IEC 309 industrial socket.

- Rack based cooling system (Technical specifications section 4.0 and 4.1)

  - Only temperature monitoring should be implemented.

- Corrections to tender text

  - Page 3 of 21, Point 1.A.b.i, the words “for HPC Clusters” stands deleted

  - Page 3 of 21, Point 1.B the word “bidder” is changed to read as “bidder/OEM”

  - Page 3 of 21, Point 1.B the word “bidder” is changed to read as “bidder/OEM”

  - Page 3 of 21, Point 1.B the words “… a server room/datacenter for HPC systems….” is changed to read as “server room/datacenter systems”

  - Page 4 of 21, point 3.g. the word “HPC” stands deleted.